{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Blad1"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Blad1","index":0,"n_rows":55,"n_cols":19,"rows_kept":55,"cut":false,"hidden":false,"merged":[[1,9,1,10],[9,3,9,5],[3,1,3,3],[25,12,25,14],[7,16,7,18],[4,8,4,12]]}
[]
[null,null,null,null,null,null,null,null,null,"Conversion F to C",null,338,"Fahrenheit"]
[null,null,null,null,null,null,null,null,null,null,null,{"$f":"(L2-32)/9*5","v":170},"Celsius"]
[null,"Buiten / outside"]
[null,"p Buiten",1,"Bara",null,null,null,null,"Stoom naar heater   Steam to heater"]
[null,"p Outside",{"$f":"C5","v":1},"Bara",null,null,null,null,"p",5,"Bara","Verz. Temp",{"$f":"Tsat_p(J6)","v":151.83624387684512}]
[null,"t Buiten",21,"oC",null,null,null,null,"t",180,"oC","Sat temp",{"$f":"Tsat_p(J6)","v":151.83624387684512}]
[null,"t outside",{"$f":"C7","v":21},"oC",null,null,null,null,"h",{"$f":"h_pt(J6,J7)","v":2812.4499724684069},"kJ/kg",null,null,null,null,null,"Condensor  Condenser"]
[null,null,null,null,null,null,null,null,"Mass/sec",6,"kg/s",null,null,null,null,null,"p",0.05,"Bara"]
[null,null,null,"Suppletie / Suppletion",null,null,null,null,null,{"$f":"J9*3.6","v":21.6},"T/h",null,null,null,null,null,"t",{"$f":"Tsat_p(R9)","v":32.875489523760166},"oC"]
[null,null,null,"mass/s",2,"kg/s",null,null,null,null,null,null,null,null,null,null,"Mass/sec",33,"kg/s"]
[null,null,null,"t",20,"oC"]
[]
[null,null,null,null,null,"mass/sec",{"$f":"R11+J9","v":39},"kg/s"]
[null,null,null,null,null,"h",{"$f":"(J9*(J8-K21)+R11*O18)/(R11+J9)","v":450.76504485257215},"kJ/kg"]
[null,null,null,null,null,"t",{"$f":"G15/4.2","v":107.32501067918383},"oC"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"h",{"$f":"hL_p(R9)","v":137.76511898849057},"kJ/kg"]
[]
[]
[null,"Ontsnap stoom escape steam",null,null,null,null,null,null,null,null,{"$f":"hL_p(J6)","v":640.18533536338612},"kJ/kg"]
[null,"m =",{"$f":"C25*PI()/4*(C24*10^-3)^2*0.85*C26/C27","v":0.12993950516296465},"kg/s"]
[null,"Q =",{"$f":"C22*(C28-C29)+C22*4.2*(H34-C7)","v":344.11954353124759},"kW"]
[null,"d =",10,"mm"]
[null,"Pijpen",2,"Stuks"]
[null,"v =",{"$f":"IF(SQRT(2*(H33-C5)*10^5*C27)>=450,450,SQRT(2*(H33-C5)*10^5*C27))","v":450},"m/s",null,null,null,null,null,null,null,null,"Stoom Steam supply"]
[null,"SV =",{"$f":"vV_p(H33)","v":0.46239178319596702},"m3/kg",null,null,null,null,null,null,null,null,"p",7,"Bara"]
[null,"h stoom",{"$f":"hV_p(H33)","v":2738.0566229312803},"kJ/kg",null,null,null,null,null,null,null,null,"t",180,"oC"]
[null,"h water",{"$f":"hL_p(H33)","v":604.72347415314596},"kJ/kg",null,null,null,null,null,null,null,null,"h",{"$f":"h_pt(N27,N28)","v":2799.3780642311017},"kJ/kg"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Mass/sec",{"$f":"((G14+E11)*4.2*(H34-G55))/(N29-C29)+C22","v":3.3114157450404984},"kg/s"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"N30*3.6","v":11.921096682145794},"T/h"]
[]
[null,null,null,null,null,null,"p",4,"Bara"]
[null,null,null,null,null,null,"t",{"$f":"Tsat_p(H33)","v":143.61253299838268},"oC"]
[null,null,null,null,null,null,"h",{"$f":"hL_p(H33)","v":604.72347415314596},"kJ/kg"]
[null,null,null,null,null,null,"Mass/sec",{"$f":"E11+G14+N30-C22","v":44.181476239877533},"kg/s"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,{"$f":"(E11*E12+G14*G16)/(E11+G14)","v":103.06525406068707}]